| Tender specification for UVC Disinfection system AQUAFIDES type 1 AF300 T |
| --- |
| The unit is validated according to following testing basics: DVGW W 294-2 (01.06.2009) BGA KTW (07.01.1977) DVGW model certificate DW-9181BU0070 |
| System type: | 1 AF300 T |
| System design: | Single lamp system - COMPACT T |
| Flow rate certified: | 5,0 - 18,7 m3/h |
| UVC-Transmission certified @ 254 nm on 10mm: | 75,5 - 96,5 % |
| UVC SSK certified @254nm | 12,22 – 1,55 mˉ¹ |
| Operating range UVC-Transmission @ 254nm on 10mm: | 75,5 - 100 % |
| Fluenz-biodosimetric (W 294-2): | 400 Joule / m2 |
| Head loss Q-max certified (without geodetical height): | 0,032 bar |
| 1 item UVC irradiation chamber |  |
| Material: | Stainless steel 1.4404 |
| Irradiation chamber connector: | DN 65, Z - design |
| Width: | 366 mm |
| Height / length (regulated by fitting position): | 1.163 mm |
| Depth: | 185 mm |
| Required height / length incl. quartz tube dismounting: | 2.355 mm |
| Maximal operating pressure: | 10 bar |
| Irradiation chamber protection class: | IP 65 |
| Temperature of process water: | 0 - 65 °C |
| 1 item UVC low pressure lamp |  |
| Type: | AF300A |
| Power consumption (incl. EVG): | 275 Watt |
| UVC lamp power after 8.760 h: | 56,0 Watt |
| Lamp service life: | 12.000 h |
| 1 item UVC sensorsystem |  |
| Numbers of UVC sensors: | 1 piece |
| Design: | according to ÖNORM M5873-1E |
| Output signal (switchable): | 0/4 - 20 mA |
| Temperature stability: | 0 - 75 °C |
| UVC measurement range: | 2 - 500 W/m² |
| Exactness of the measurement: | +/- 2% |
| Selectivity @ 254 nm: | ≥ 99% |
| UVC sensor cable length: | 5 m |
| 1 item control cabinet |  |
| Control mode: | digital |
| Control data and software update access: | USB |
| Software service and settings: | via laptop |
| Material of control cabinet: | aluminium |
| Colour of control cabinet: | grey RAL 7040 |
| Weigth: | 5,2 kg |
| Dimensions (WxHxD): | 330 x 200 x 120 mm |
| Operating voltage (nominal voltage): | 230 Volt / 50 Hz |
| Total power consumption: | 275 Watt |
| Protection class: | IP 65 |
| Environmental temperature control box: | 5 - 35 °C |
| UVC lamp cable length: | 4 m |
| Power line cable length: | 2,5 m |