| Tender specification for UVC Disinfection system AQUAFIDES Typ 6 AF300 T |
| --- |
| Validated regarding ÖNORM M 5873-1E - method B type tested This validated system must only be equipped with a plant UVC sensor and don´t must have a UV-transmittance (254nm) measuring device when the system is installed. ÖVGW Quality mark with the registration number W 1.578 |
| System type: | 6 AF300 T |
| System design: | Multiple lamp system COMPACT T |
| Flow rate certified: | 51 - 232 m3/h |
| UV-Transmission certified @ 254nm on 100mm: | 10 - 70 % |
| Operating range UV-Transmission @ 254nm on 100mm: | 10 - 100 % |
| Fluenz-biodosimetric (ÖNORM M 5873-1): | 400 Joule / m2 |
| Head loss Q-max certified: (without geodetical height) | 0,071 bar |
| 1 item UVC irradiation chamber |  |
| Material: | Stainless steel 1.4404 |
| Irradiation chamber connectors: | DN 200, U - design |
| Width: | 500 mm |
| Height / length (regulated by fitting position): | 1.134 mm |
| Depth: | 390 mm |
| Required height/length incl. quartz tube dismounting: | 2.365 mm |
| Maximal operating pressure: | 10 bar |
| Irradiation chamber protection class: | IP 65 |
| Temperature of process water: | 0 - 65 °C |
| 6 item UVC low pressure lamps |  |
| Type: | AF300A |
| Power consumption (incl. EVG): | 270 Watt |
| UVC lamp power after 8.760 h: | 55 Watt |
| Lamp service life: | 12.000 h |
| 1 item UVC sensorsystem |  |
| Numbers of UVC sensors: | 1 piece |
| Design: | According to ÖNORM M5873-1E |
| Output signal (switchable): | 0/4 - 20 mA |
| Temperature stability: | 0 - 75 °C |
| UVC measurement range: | 2 - 500 W/m² |
| Exactness of the measurement: | ± 2 % |
| Selectivity @ 254 nm: | ≥ 99 % |
| UVC sensor cable length: | 9 m |
| 1 item control cabinet |  |
| Control mode: | digital |
| Control data and software update access: | USB |
| Software service and settings: | Via Laptop |
| Material of control cabinet: | Sheet steel coated |
| Colour of control cabinet: | grey RAL 7035 |
| Weigth: | 67 kg |
| Dimensions (WxHxD): | 760 x 760 x 300 mm |
| Operating voltage (nominal voltage): | 230 Volt / 50 Hz |
| Total power consumption: | 1.650 Watt |
| Protection class: | IP 55 |
| Environmental temperature control box: | 5 - 35 °C |
| UVC lamp cable length: | 8 m |
| Power line cable length: | on site |